SEQUENCE OF OPERATIONS

SAMPLE AIR HANDLING UNIT

SECTION: 23 00 00

TYPE OF DOCUMENT: Mechanical Specification – SEQUENCE OF OPERATIONS

REVISION NUMBER: A

PART 1 – System Description

This sample describes a fictional single-duct air-handling unit serving an open office floor. It exists to exercise the parser and is not a real specification.

The air-handling unit shall include the following major components:

- A variable-speed supply fan with a VFD.

- A chilled-water cooling coil with a modulating two-way valve.

- A heating coil, where provided, with a modulating two-way valve.

- A mixed-air section with outside-air and return-air dampers.

PART 2 – Definitions and Operating Modes

The following abbreviations apply to this section:

- AHU — air-handling unit.

- SAT — supply-air temperature.

- OA — outside air.

- VFD — variable-frequency drive.

The unit shall be considered occupied when all of the following are true:

- The BMS time-of-day schedule is in its occupied period.

- No unoccupied override is active.

PART 3 – Adjustable Setpoints

Setpoints listed below are adjustable through the BMS operator interface.

| Setpoint | Initial Value |
| --- | --- |
| Supply Air Temperature Setpoint | 55 °F |
| Minimum Outside-Air Damper Position | 20 % |
| Economizer Changeover Temperature | 65 °F |
| Cooling Stage Delay | [___ s] |

PART 4 – Availability

The air-handling unit shall be considered available when:

- The local hand-off-auto selector is in the AUTO position.

- No fire-alarm shutdown signal is present.

- The supply-fan VFD reports no active fault.

- BMS communication with the unit controller is healthy.

PART 5 – Start-Up Sequence

Upon a call for cooling, the BMS shall execute the following sequence:

- Open the outside-air damper to its minimum position.

- Start the supply fan at minimum speed.

- Prove airflow through the supply-fan status input.

- Enable the supply-air temperature control loop.

PART 6 – Capacity Staging

An additional stage of cooling shall be enabled when one or more of the following conditions persist for the adjustable staging delay:

- The supply-air temperature remains above its setpoint by more than 2 °F.

- The chilled-water valve remains fully open.

- Zone cooling demand remains above 80 %.

PART 9 – Loss of BMS Communication

Where BMS communication is lost, the unit shall:

- Maintain the last commanded supply-air temperature setpoint.

- Revert to local stand-alone control after 5 minutes.

- Annunciate a communications-failure alarm at the BMS.

The following applies during a communications outage.

- Trend data shall continue to be buffered in the unit controller.

- The unit shall not shut down solely because of the outage.

PART 10 – Power Failure and Restoration

Following restoration of normal power, the unit shall:

- Remain off until the BMS commands a restart.

- The unit should resume its previous operating mode once restarted.

- Annunciate a power-failure alarm that may be cleared manually.

PART 11 – Alarms

An alarm shall be annunciated when any of the following occur:

- Supply-air temperature deviates from setpoint by more than 5 °F for 10 minutes.

- The supply fan is commanded on but airflow is not proven.

- The unit controller loses communication with the BMS.

PART 12 – BMS Trending

The BMS shall trend the following points:

• Supply-air temperature.

• Supply-duct static pressure.

• Supply-fan speed command.

Outside-air damper position feedback

END OF SECTION